Chapter 03: Manufacture, Storage, and Transport of Medical Gases

MULTIPLE CHOICE

1.	Which of the following gases support combustion?

Air

Oxygen

Helium

Carbon Dioxide

| a. | 2 only | c. | 2, 3 |
| --- | --- | --- | --- |
| b. | 1, 2 | d. | 1, 3, 4 |

ANS:	B

Oxygen and air support combustion.    Helium and carbon dioxide are not flammable

PTS:	1	REF:	Page 57, Table 3-2

2.	Which of the following gases is the least dense?

| a. | Carbon dioxide | c. | Helium |
| --- | --- | --- | --- |
| b. | Nitrous oxide | d. | Air |

ANS:	C

Helium is the second-lightest element, with a density of 0.165 kg/m3 at 21.1° C and 1 atmospheric pressure (atm). Oxygen is slightly heavier than air, with a density of 1.326 kg/m3 at 21.1° C and 760 mm Hg.

PTS:	1	REF:	Page 57, Table 3-3

3.	Which gas has been used successfully in the treatment of pulmonary hypertension of the newborn?

| a. | Oxygen | c. | Nitrous oxide |
| --- | --- | --- | --- |
| b. | Nitric oxide | d. | Helium-oxygen mixture |

ANS:	B

At very low concentrations (2 to 80 parts per million) combined with oxygen, nitric oxide has been used to successfully treat persistent pulmonary hypertension of the newborn. Nitrous oxide is used as a central nervous system depressant (anesthetic). Helium-oxygen mixtures decrease the work of breathing by decreasing turbulent airflow.

PTS:	1	REF:	Page 56

4.	In high concentrations, which of the following gases is a potent anesthetic?

| a. | Nitric oxide | c. | Carbon dioxide |
| --- | --- | --- | --- |
| b. | Nitrous oxide | d. | Helium-oxygen mixture |

ANS:	B

The major use for nitrous oxide is a central nervous system depressant. As such, it is a potent anesthetic when administered in high concentrations. At very low concentrations (2 to 80 parts per million) combined with oxygen, nitric oxide has been used successfully to treat persistent pulmonary hypertension of the newborn. Carbon dioxide is nonflammable, but it supports combustion. Helium-oxygen mixtures decrease the work of breathing by decreasing turbulent airflow.

PTS:	1	REF:	Page 56

5.	Which of the following gases is used to decrease the work of breathing associated with severe airway obstruction?

| a. | Nitric oxide | c. | Helium-oxygen mixture |
| --- | --- | --- | --- |
| b. | Nitrous oxide | d. | Carbon dioxide–oxygen mixture |

ANS:	C

A helium-oxygen mixture decreases the work of breathing by decreasing turbulent airflow.

PTS:	1	REF:	Page 56

6.	Chemical pneumonitis and pulmonary edema can be caused by which of the following?

| a. | Nitrous oxide |
| --- | --- |
| b. | Carbon dioxide |
| c. | Excess amounts of nitric oxide |
| d. | A combination of nitric oxide and nitrogen dioxide |

ANS:	D

Nitric oxide and nitrogen dioxide combine to form a potent irritant that can cause chemical pneumonitis and pulmonary edema. Nitrous oxide, which is nicknamed laughing gas, can cause brain damage or death if inhaled without a sufficient oxygen supply.

PTS:	1	REF:	Page 56

7.	Carbon dioxide can be obtained by which of the following methods?

| a. | Heating uranium ore |
| --- | --- |
| b. | Combustion of natural gas |
| c. | Fractional distillation of liquid air |
| d. | Oxidizing ammonia at high temperatures |

ANS:	B

Unrefined carbon dioxide can be obtained from the combustion of coal, natural gas, or other carbonaceous fuels. Helium can be obtained by heating uranium ore. The two methods most commonly used to prepare oxygen are the fractional distillation of liquid air and the physical separation of atmospheric air. Nitric oxide can be prepared by oxidizing ammonia at high temperatures (i.e., 500 C and above).

PTS:	1	REF:	Page 55

8.	Which agency is responsible for the regulations that govern the manufacture, storage, and transport of compressed gases?

| a. | Bureau of Medical Devices |
| --- | --- |
| b. | Compressed Gas Association (CGA) |
| c. | U.S. Department of Transportation (DOT) |
| d. | U.S. Food and Drug Administration (FDA) |

ANS:	C

Metal cylinders have been used for storing compressed gases since 1888. Federal regulations issued by the DOT require that all cylinders used to store and transport compressed gases conform to specifications. The FDA sets purity standards for medical gas. The CGA provides standards and safety systems for compressed gas systems.

PTS:	1	REF:	Page 57

9.	Which agency sets purity standards for medical gases?

| a. | CGA |
| --- | --- |
| b. | DOT |
| c. | FDA |
| d. | International Standards Organization (ISO) |

ANS:	C

The FDA sets purity standards for medical gas. The DOT governs the manufacture, storage, and transport of compressed gases. The CGA sets standards and provides safety systems for compressed gas systems. The ISO is an international agency that sets standards for technology.

PTS:	1	REF:	Page 55, Box 3-2

10.	Safety systems for medical gases are recommended and provided by:

| a. | DOT. |
| --- | --- |
| b. | CGA. |
| c. | FDA. |
| d. | National Fire Protection Association (NFPA). |

ANS:	B

The CGA sets standards and provides safety systems for compressed gas systems. The FDA sets purity standards for medical gas. The DOT regulates the manufacture, storage, and transport of compressed gases. The NFPA is an independent agency that provides information on fire protection and safety.

PTS:	1	REF:	Page 54, Box 3-2

11.	A cylinder has “DOT 3AA 2015” stamped on it. What does the 3AA stand for?

| a. | Ownership mark | c. | Non–heat-treated carbon-steel |
| --- | --- | --- | --- |
| b. | Manufacturer’s mark | d. | Heat-treated, high-strength steel |

ANS:	D

3AA stands for heat-treated, high-strength steel. Type 3A cylinders are made of carbon-steel (non–heat-treated).

PTS:	1	REF:	Page 57

12.	A cylinder has “DOT 3AL 2015” stamped on it. What does the 3AL stand for?

| a. | Manufacturer’s initials |
| --- | --- |
| b. | Constructed of heat-treated, high-strength steel |
| c. | Required to undergo hydrostatic testing every 3 years |
| d. | Constructed of specially prescribed seamless aluminum alloys |

ANS:	D

3AL means that the cylinder is constructed of specially prescribed seamless aluminum alloys and must be examined every 5 years to test its expansion characteristics. Type 3AA is constructed of heat-treated, high-strength steel.

PTS:	1	REF:	Page 57

13.	Which type of cylinder is produced from non–heat-treated carbon-steel?

| a. | 3 | c. | 3AA |
| --- | --- | --- | --- |
| b. | 3A | d. | 3AAA |

ANS:	B

3AA means heat-treated, high-strength steel; 3 and 3AAA are not applicable.

PTS:	1	REF:	Page 56

14.	If the maximum filling pressure is marked as 2050 lb-force per square inch gauge (psig), this cylinder is capable of holding _____ psig.

| a. | 1845 | c. | 2255 |
| --- | --- | --- | --- |
| b. | 2050 | d. | 2460 |

ANS:	C

Compressed gas cylinders should be capable of holding up to 10% more than the maximum filling pressure as marked. 10%  2050 = 205 + 2050 = 2255 psig.

PTS:	1	REF:	Page 57

15.	An asterisk following the reexamination date on a cylinder indicates that the cylinder:

| a. | has passed the test. | c. | must be retested every 10 years. |
| --- | --- | --- | --- |
| b. | must be retested every 5 years. | d. | has been sold to another company. |

ANS:	C

An asterisk after the reexamination date on the cylinder markings (see Figure 3-4) indicates that the cylinder must be retested every 10 years.

PTS:	1	REF:	Page 57

16.	Which size cylinder would be most appropriate for use during patient transport?

| a. | H | c. | M |
| --- | --- | --- | --- |
| b. | G | d. | E |

ANS:	D

Size “E” cylinders are used for emergencies and for transport. The other cylinders are too large to be used for transport.

PTS:	1	REF:	Page 60

17.	Which of the following is not marked on a cylinder?

| a. | Ownership marks |
| --- | --- |
| b. | Method of production |
| c. | Serial number of the cylinder |
| d. | Type of material used to construct the cylinder |

ANS:	B

The method of production is not required to be on the cylinder. All the other options are a requirement.

PTS:	1	REF:	Pages 60-61

18.	A plus sign after an examination date indicates that the cylinder:

| a. | may be retested in 5 years. |
| --- | --- |
| b. | may be retested in 10 years. |
| c. | has been sold to another company. |
| d. | has complied with the requirements of the test. |

ANS:	D

The plus sign means that the cylinder has complied with the requirements of the test. An asterisk following the reexamination date on the cylinder markings indicates that the cylinder must be retested every 10 years.

PTS:	1	REF:	Page 61

19.	The color codes for cylinders are prescribed by the:

| a. | U.S. National Formulary. | c. | FDA. |
| --- | --- | --- | --- |
| b. | CGA. | d. | American Standards Association. |

ANS:	A

The U.S. National Formulary sets the color-code standards.

PTS:	1	REF:	Page 61

20.	What is the cylinder color for nitrous oxide?

| a. | Red | c. | Brown |
| --- | --- | --- | --- |
| b. | Black and white | d. | Light blue |

ANS:	D

Nitrous oxide is light blue. Ethylene is red. Compressed air is black and white. Helium is brown. See Table 3-4.

PTS:	1	REF:	Page 61, Table 3-4

21.	What is the international color code for compressed air?

| a. | Gray | c. | Yellow |
| --- | --- | --- | --- |
| b. | Black | d. | Black and white |

ANS:	D

The international color code for compressed air is black and white. Yellow is the color set by the U.S. National Formulary.

PTS:	1	REF:	Page 61

22.	Which of the following appear(s) on the labels of gas cylinders?

1. Chemical symbol of the contents

2. Precautionary measures for the gas

3. Specific hazards related to use of the gas

4. Volume of the cylinder marked in liters at 70 F

| a. | 1 | c. | 1, 2, and 3 |
| --- | --- | --- | --- |
| b. | 1 and 4 | d. | 1, 2, 3, and 4 |

ANS:	D

The CGA and the American Standards Association specify that all labels should include the chemical symbol of the contents, precautionary measures, specific hazards related to the gas, and the volume of the cylinder marked in liters at 70 F.

PTS:	1	REF:	Page 62

23.	Which agency sets standards for the purity of medical gases?

| a. | U.S. National Formulary | c. | FDA |
| --- | --- | --- | --- |
| b. | CGA | d. | American Standards Association |

ANS:	C

Only the FDA sets the purity standards for medical gases.

PTS:	1	REF:	Page 62

24.	A 97% purity standard is required for which of the following gases?

| a. | Ethylene | c. | Nitric oxide |
| --- | --- | --- | --- |
| b. | Nitrogen | d. | Nitrous oxide |

ANS:	D

See Table 3-4.

PTS:	1	REF:	Page 61, Table 3-4

25.	What is the purity standard for oxygen?

| a. | 99% | c. | 97% |
| --- | --- | --- | --- |
| b. | 98% | d. | 95% |

ANS:	A

See Table 3-4.

PTS:	1	REF:	Page 61, Table 3-5

26.	Which of the following statement(s) is (are) true about cylinder valves?

1. Diaphragm valves can withstand pressure greater than 1500 psig.

2. Direct-acting valves are used for pressure less than 1500 psig.

3. Diaphragm valves should be used with flammable gases.

4. Leakage cannot occur with direct-acting valves.

| a. | 3 | c. | 2 and 3 |
| --- | --- | --- | --- |
| b. | 1 | d. | 1 and 4 |

ANS:	A

Diaphragm valves can withstand pressures less than 1500 psig and should be used with flammable gases because they do not allow leaks. A direct-acting valve contains two washers and a Teflon packing to prevent gas leakage around the threads.

PTS:	1	REF:	Page 63

27.	Which of the following statement(s) is (are) not true about cylinder valves?

1. Diaphragm valves cannot withstand pressure greater than 1500 psig.

2. Direct-acting valves are used for pressure greater than 1500 psig.

3. Diaphragm valves should not be used with anesthetic gases.

4. Stem leakage can occur with direct-acting valves.

| a. | 3 | c. | 1 and 4 |
| --- | --- | --- | --- |
| b. | 2 and 4 | d. | 1, 2, and 3 |

ANS:	A

Diaphragm valves are ideal for situations in which no gas leaks can be allowed, such as with flammable anesthetics.

PTS:	1	REF:	Page 63

28.	Which of the following statement(s) is (are) true about diaphragm type of valves?

1. A partial rotation of a diaphragm type of valve will not open the stem.

2. The valve seat in a diaphragm type of valve does not turn.

3. The diaphragm type of valve contains two fiber washers.

4. The diaphragm type of valve uses a threaded stem.

| a. | 2 | c. | 3 and 4 |
| --- | --- | --- | --- |
| b. | 1 and 4 | d. | 2 and 4 |

ANS:	D

The valve seat does not turn and is therefore resistant to scoring; it also uses a threaded stem in place of the packing found on the direct-acting valves. The direct-acting valve has two fiber washers.

PTS:	1	REF:	Page 63

29.	The diaphragms of a diaphragm type of valve are made of:

1. steel.

2. copper.

3. aluminum.

4. chrome-molybdenum.

| a. | 2 | c. | 3 and 4 |
| --- | --- | --- | --- |
| b. | 2 and 3 | d. | 1 and 2 |

ANS:	D

The diaphragm type of valve has two diaphragms, one made of steel and one made of copper. Aluminum and chrome-molybdenum are metals that are used in the construction of cylinders.

PTS:	1	REF:	Page 63

30.	Wood’s metal is used to make:

| a. | gas cylinders. |
| --- | --- |
| b. | fusible-plug pressure-relief valves. |
| c. | rupture-disk pressure-relief valves. |
| d. | spring-loaded pressure-relief devices. |

ANS:	B

Fusible-plug pressure-relief valves are made of a metal alloy that melts when the temperature of the gas in the tank exceeds a predetermined temperature. This is called Wood’s metal.

PTS:	1	REF:	Page 64

31.	Which type of valve operates on the principle that as the pressure in a cylinder increases, the temperature of the gas increases?

| a. | Direct-acting valves | c. | Rupture-disk pressure-relief valves |
| --- | --- | --- | --- |
| b. | Fusible-plug pressure-relief valves | d. | Spring-loaded pressure-relief valves |

ANS:	B

Fusible-plug pressure-relief valves operate on the principle that as the pressure in a tank increases, the temperature of the gas increases, causing the plug to melt. Spring-loaded devices are designed to release excessive cylinder pressure and reseal, preventing further release of gas from the cylinder after the cause of the excessive pressure is removed. The rupture-disk will buckle when the pressure inside the cylinder exceeds a certain predetermined limit. Direct-acting valves are not pressure-relief valves; instead, they are controlling devices that seal the contents of a compressed cylinder until it is ready for use.

PTS:	1	REF:	Page 58, Box 3-2

32.	Which agency designed the safety systems for outlet connections of cylinder valves?

| a. | Z-79 Committee |
| --- | --- |
| b. | CGA |
| c. | FDA |
| d. | American National Standards Institute (ANSI) |

ANS:	B

The CGA designed the safety systems for outlet connections of cylinders. The Z-79 Committee establishes standards for anesthetic and ventilatory devices. The FDA sets purity standards. ANSI is a private nonprofit organization that coordinates the voluntary development of national standards in the United States.

PTS:	1	REF:	Page 64

33.	Medical gas cylinder valve outlets always have connections that are _____-handed and _____.

| a. | right; external | c. | left; external |
| --- | --- | --- | --- |
| b. | right; internal | d. | left; internal |

ANS:	A

External and right-handed is the standard for medical gas cylinder valve outlets.

PTS:	1	REF:	Page 66

34.	Which safety system is used with small cylinders, sizes “A” through “E”?

| a. | Pin Index Safety System |
| --- | --- |
| b. | Diameter Index Safety System |
| c. | Direct-Acting Valve Safety System |
| d. | American Standard Index Safety System |

ANS:	A

Small cylinders (i.e., sizes “A” to “E”) with post type of valves use a different American Standard indexing system called the Pin Index Safety System.

PTS:	1	REF:	Page 65, Figure 3-8

35.	The cylinder outlet diameter for a “G” size oxygen cylinder is _____ inches.

| a. | 0.830 | c. | 0.960 |
| --- | --- | --- | --- |
| b. | 0.903 | d. | 0.965 |

ANS:	B

See Figure 3-8.

PTS:	1	REF:	Page 65, Figure 3-8

36.	A nitrous oxide “H” size cylinder cannot be attached to oxygen equipment because the nitrous oxide cylinder has which of the following?

1. A different outlet size

2. A different thread type

3. An outer threading system

4. Internal threading; and oxygen has an external threading

| a. | 1, 2, 3, and 4 | c. | 2 and 3 |
| --- | --- | --- | --- |
| b. | 2, 3, and 4 | d. | 1 and 2 |

ANS:	D

See Figure 3-8.

PTS:	1	REF:	Page 65, Figure 3-8

37.	Which of the following types of threading does a compressed air cylinder have?

1. Right-handed

2. Left-handed

3. Internal

4. External

| a. | 2 and 3 | c. | 2 and 4 |
| --- | --- | --- | --- |
| b. | 1 and 4 | d. | 1 and 3 |

ANS:	B

See Figure 3-8.

PTS:	1	REF:	Page 66, Figure 3-9

38.	What are the pin positions for an “E” size oxygen cylinder?

| a. | 2 and 4 | c. | 2 and 6 |
| --- | --- | --- | --- |
| b. | 2 and 5 | d. | 3 and 5 |

ANS:	B

See Figure 3-9.

PTS:	1	REF:	Page 66, Figure 3-9

39.	What are the pin positions for an “E” size compressed air cylinder?

| a. | 1 and 5 | c. | 2 and 5 |
| --- | --- | --- | --- |
| b. | 1 and 6 | d. | 3 and 5 |

ANS:	A

See Figure 3-9.

PTS:	1	REF:	Page 66, Box 3-4

40.	Which of the following procedures should be followed in setting up a compressed gas cylinder at a patient’s bedside?

1. Inspect the cylinder and valve for dirt, debris, and oil.

2. Make sure the cylinder is properly secured.

3. Tighten the regulator with a pipe wrench.

4. Open the cylinder valve completely.

| a. | 3 and 4 | c. | 1, 2, 3, and 4 |
| --- | --- | --- | --- |
| b. | 1 and 2 | d. | 1, 2, and 4 |

ANS:	B

See Box 3-4.

PTS:	1	REF:	Page 66, Box 3-4

41.	The best position for the cylinder valve when it is being used is:

| a. | completely open. |
| --- | --- |
| b. | two turns toward the left. |
| c. | one turn, open toward the right. |
| d. | one half-turn back from completely open. |

ANS:	D

See Box 3-4.

PTS:	1	REF:	Page 67

42.	After connecting an oxygen regulator to an “H” cylinder and turning the direct-acting valve on, the respiratory therapist attempts to turn on the flow of oxygen. The desired gas flow is not achieved. Which of the following is (are) the most likely problem(s)?

1. The therapist is using the wrong regulator.

2. The pressure in the cylinder is inadequate.

3. The regulator outlet is obstructed.

4. There is a leak in the connection between the cylinder outlet and the regulator.

| a. | 1 | c. | 2 and 3 |
| --- | --- | --- | --- |
| b. | 2 and 4 | d. | 1, 2, and 4 |

ANS:	C

Failure to achieve a desired gas flow from a cylinder regulator can result from inadequate pressure or from an obstruction at the regulator outlet. There would be a hissing noise if there was a leak. Safety systems prevent the wrong regulator from fitting an oxygen cylinder.

PTS:	1	REF:	Page 67

43.	An “E” size cylinder is turned on, and the flowmeter is off. Which of the following is (are) the most likely cause(s) of a hissing sound?

1. A cracked flowmeter

2. Inadequate pressure in the cylinder

3. An obstruction at the regulator outlet

4. A leak in the connection between the yoke and the cylinder opening

| a. | 2 | c. | 1 and 3 |
| --- | --- | --- | --- |
| b. | 1 and 2 | d. | 1 and 4 |

ANS:	D

A hissing noise means that there is a leak somewhere in the system. Typically, that will occur between the yoke and the cylinder opening or if there is a crack in the flowmeter. Inadequate pressure or an obstruction would not cause a hissing sound.

PTS:	1	REF:	Page 67

44.	A full “H” size cylinder is used to provide oxygen to an air-entrainment mask at 6 L/min. If the cylinder is replaced at 500 psig, how long will it last?

| a. | 5 hours | c. | 10 hours 50 minutes |
| --- | --- | --- | --- |
| b. | 10 hours 20 minutes | d. | 15 hours 23 minutes |

ANS:	D

Amount of time left in cylinder = (cylinder pressure  cylinder factor)/flow rate of gas (liters/minute). H cylinder factor = 3.14. Full-size “H” cylinder = 2265 psig. If the cylinder is changed at 500 psi, then 2265 – 500 = 1765 (1765 psi will be used). (3.14  1765)/6 L/min = 923.7 minutes/60 = 15 hours (0.39  60) = 15 hours 23 minutes.

PTS:	1	REF:	Page 67, Box 3-5

45.	An “E” size cylinder with 1600 psig is used to provide oxygen to a simple mask running at 5 L/min during a transport. The cylinder will last:

| a. | 8 hours. | c. | 68 minutes. |
| --- | --- | --- | --- |
| b. | 56 minutes. | d. | 89 minutes. |

ANS:	D

Amount of time left in cylinder = (cylinder pressure  cylinder factor)/flow rate of gas (liters/minute). “E” size factor = 0.28. A simple mask should run at a minimum of 5 L/min. Therefore, (1600  0.28)/5 L/min = 448/5 = 89.6 minutes.

PTS:	1	REF:	Page 67, Box 3-5

46.	An “E” size oxygen cylinder with 2000 psig in it is being used at 4 L/min. How much will be used in 45 minutes?

| a. | 26.2 psig | c. | 180 psig |
| --- | --- | --- | --- |
| b. | 140 psig | d. | 643 psig |

ANS:	D

Amount of time left in cylinder = (cylinder pressure  cylinder factor)/flow rate of gas (liters/minute). (2000  0.28)/4 = 140 minutes to use up 2000 psig. Therefore, 2000 psig/140 min = X psig/1 minute X = 14.3 psig/min  45 minutes = 642.8 psig.

PTS:	1	REF:	Page 67, Box 3-5

47.	A “G” size oxygen cylinder with 1450 psig is being used at 5 L/min. This cylinder will be empty in approximately _____ hour(s) and _____ minutes.

| a. | 1; 30 | c. | 11; 30 |
| --- | --- | --- | --- |
| b. | 2; 39 | d. | 15; 16 |

ANS:	C

Amount of time left in cylinder = (cylinder pressure  cylinder factor)/flow rate of gas (liters/minute). “G” size cylinder factor = 2.41. Amount of time = (1450  2.41)/5 = 698.9 minutes/60 = 11 hours 39 minutes.

PTS:	1	REF:	Page 67, Box 3-5

48.	The K cylinder at a patient’s bedside contains 1300 psig and is using 7 L/min. It will take approximately _____ hours to use 800 psig.

| a. | 3.7 | c. | 6 |
| --- | --- | --- | --- |
| b. | 9.7 | d. | 4 |

ANS:	C

Amount of time left in cylinder = (cylinder pressure  cylinder factor)/flow rate of gas (liters/minute). K factor = 3.14. Time to use 800 psi = (800  3.14)/7 = 358.8 min/60 = 5 hours 59 minutes.

PTS:	1	REF:	Page 57, Box 3-5

49.	The E cylinder on a crash cart contains 900 psig. How long would the cylinder last if used at 10 L/min?

| a. | 1 hour | c. | 3 hours 36 minutes |
| --- | --- | --- | --- |
| b. | 25 minutes | d. | 4 hours 42 minutes |

ANS:	B

Amount of time left in cylinder = (cylinder pressure  cylinder factor)/flow rate of gas (liters/minute). E factor = 0.28. Time to use 900 psig = (900  0.28)/10 = 25 minutes.

PTS:	1	REF:	Page 67, Box 3-5

50.	A “G” size cylinder with 2000 psig is used for 6 hours at 5 L/min. How much gas was used during this time?

| a. | 2000 psig | c. | 573 psig |
| --- | --- | --- | --- |
| b. | 750 psig | d. | 107 psig |

ANS:	B

Amount of time left in cylinder = (cylinder pressure  cylinder factor)/flow rate of gas (liters/minute). G factor = 2.41. Time to use 2000 psig = (2000  2.42)/5 = 964 minutes/60 = 16 hours. 2000 psig /16 hours = X psig/6 hours. X = 750 psig will be used in 6 hours at 5 L/min.

PTS:	1	REF:	Page 67, Box 3-5

51.	Which of the following statements is (are) true with regard to liquid bulk systems?

1. Liquefied oxygen occupies a fraction of the space required for the storage of gaseous oxygen.

2. The CGA regulates the construction of liquid oxygen systems.

3. A bulk oxygen system contains more than 40,000 ft of oxygen.

4. The working pressure of a liquid bulk oxygen system is 50 psig.

| a. | 2 | c. | 1 and 3 |
| --- | --- | --- | --- |
| b. | 3 and 4 | d. | 1 and 4 |

ANS:	D

See Box 3-6.

PTS:	1	REF:	Page 68, Box 3-6

52.	The function of the vaporizer of a liquid bulk oxygen system is to:

| a. | act as a pressure release. |
| --- | --- |
| b. | reduce the pressure to 50 psig. |
| c. | convert liquid oxygen to gaseous oxygen. |
| d. | allow heat to be released into the environment. |

ANS:	C

The reservoir stores a mixture of liquid and gaseous oxygen. The vaporizer acts as a heat exchanger where heat is absorbed from the environment and used to warm the liquid oxygen to room temperature, thus forming gaseous oxygen.

PTS:	1	REF:	Page 67

53.	The gas above liquid oxygen is maintained:

| a. | between its freezing point and its critical temperature. |
| --- | --- |
| b. | between its boiling point and its critical temperature. |
| c. | at its critical pressure. |
| d. | at its boiling point. |

ANS:	B

The pressure-release valve allows some of the gas on top of the liquid to escape if the contents are warmed too much. This release of gas allows the gas within the container to expand, thus lowering the temperature. This maintains the gas under pressure between its boiling point and its critical temperature so that the majority of the reservoir’s contents will be maintained in the liquid state.

PTS:	1	REF:	Page 67

54.	The application of Gay-Lussac’s law in a bulk liquid oxygen system:

| a. | accounts for the conversion of the liquid oxygen to gaseous oxygen. |
| --- | --- |
| b. | allows the reservoir contents to be maintained in the liquid state. |
| c. | keeps the liquid oxygen above its critical temperature. |
| d. | allows the gas to be maintained at 50 psig. |

ANS:	B

According to Gay-Lussac’s law, if the volume of a gas remains constant, there is a direct relationship between the absolute pressure of a gas and its temperature. This release of gas allows the gas within the container to expand, thus lowering the temperature.

PTS:	1	REF:	Page 67

55.	Which of the following are components of a bulk liquid oxygen system?

1. 3AA container

2. Insulated reservoir

3. Pressure-release valve

4. A heater for the liquid oxygen

| a. | 2 and 3 | c. | 2 and 4 |
| --- | --- | --- | --- |
| b. | 1 and 3 | d. | 1 and 4 |

ANS:	A

A bulk liquid oxygen system consists of an insulated reservoir, a vaporizer with associated tubing attached to the reservoir, a pressure-reducing valve, and an appropriate pressure-release valve.

PTS:	1	REF:	Page 67

56.	The NFPA requires bulk oxygen systems to be located:

1. 10 feet from flammable gas storage.

2. 10 feet from public sidewalks.

3. 5 feet from the property line.

4. 5 feet from congested areas.

| a. | 1 and 4 | c. | 2, 3, and 4 |
| --- | --- | --- | --- |
| b. | 2 and 3 | d. | 1, 2, 3, and 4 |

ANS:	B

See Box 3-6.

PTS:	1	REF:	Page 70, Figure 3-11

57.	According to the NFPA, for a nonambulatory patient, the minimum distance from a bulk oxygen supply is _____ feet.

| a. | 5 | c. | 25 |
| --- | --- | --- | --- |
| b. | 10 | d. | 50 |

ANS:	D

See Figure 3-11.

PTS:	1	REF:	Page 70, Figure 3-11

58.	One liter of liquid oxygen weighs _____ oz.

| a. | 25 | c. | 86 |
| --- | --- | --- | --- |
| b. | 40 | d. | 860 |

ANS:	B

One liter of oxygen weighs 2.5 lb. 2.5 lb  16 oz/lb = 40 oz.

PTS:	1	REF:	Page 69

59.	A home care patient inquires about how long her portable liquid oxygen system, currently weighing 30 lb, will last if she uses 3 L/min. The manufacturer says the weight of an empty container is 8 lb. Her system will last for _____ day(s) and _____ hours.

| a. | 1; 18 | c. | 4; 21 |
| --- | --- | --- | --- |
| b. | 2; 9 | d. | 8; 12 |

ANS:	A

First subtract 8 lb from 30 lb = 22 lb. Convert 22 lb/2.5 lb/L = 8.8 L. 8.8 L  860 (liter of liquid oxygen multiplied by 860 equals the liters of gaseous oxygen) = 7568 L. Then divide by liter flow. 7568/3 L/min = 2522 min = 1 day 18 hours.

PTS:	1	REF:	Page 70, Box 3-7

60.	If a portable liquid oxygen reservoir is set to deliver 6 L/min and the current reservoir weight is 38 lb, it will take _____ hours for the reservoir to empty if the weight of an empty container is 10 lb.

| a. | 5 | c. | 27 |
| --- | --- | --- | --- |
| b. | 23 | d. | 36 |

ANS:	C

Subtract 10 lb from 38 lb = 28 lb. Convert 28 lb/2.5 lb/L = 11.2 lb. 11.2 lb  860 = 9632 L. Then divide by liter flow: 9632 L/6 L/min = 1605 minutes, or 27 hours.

PTS:	1	REF:	Page 70, Box 3-7

61.	Approximately how long will a liquid oxygen reservoir last when supplying 3 L/min to your patient? The current reservoir weight is 20 lb, and the weight of an empty reservoir is 10 lb.

| a. | 19 hours | c. | 46 hours |
| --- | --- | --- | --- |
| b. | 38 hours | d. | 119 hours |

ANS:	A

Subtract 10 lb from 20 lb = 10 lb. Convert 10 lb/2.5 lb/L= 4 L. 4  860 = 3440 L. Then divide by the flow 3440 L/3 L/min = 1146 minutes, or 19 hours.

PTS:	1	REF:	Page 70

62.	During your home care visit on Monday morning, you weigh the patient’s portable liquid oxygen reservoir. The liquid oxygen weighs 18 lb, and the patient is using 2 L/min. When should you schedule a visit to fill up the reservoir?

| a. | The next Monday | c. | Thursday afternoon |
| --- | --- | --- | --- |
| b. | Wednesday morning | d. | Friday afternoon |

ANS:	B

18 lb/2.5 lb/L=7.2 L. 7.2 L  860 = 6192 L/2 L/min = 3096 minutes, or 51 hours 36 minutes, which is 2 days 3 hours 36 minutes. So it would have to be filled on Wednesday.

PTS:	1	REF:	Page 70, Box 3-7

63.	Which of the following types of compressor can accommodate a mechanical ventilator?

1. Diaphragm

2. Liquid air

3. Rotary

4. Piston

| a. | 1 | c. | 3 and 4 |
| --- | --- | --- | --- |
| b. | 2 and 4 | d. | 1, 3, and 4 |

ANS:	C

Rotary compressors use a rotating vane to compress air from an intake valve. As the rotating vane turns, gas is drawn into the cylinder through a one-way valve (Figure 3-16). The rotor turns, which causes the gas to be compressed as the oval-shaped cylinder becomes smaller. The compressed gas is then forced out of the compressor through another one-way outflow valve. Low-pressure rotary compressors are used in ventilators such as the Bennett MA-1. Piston compressors use the action of a motor-driven piston to compress atmospheric air. The piston is seated within a cylinder casing and is sealed to it with a carbon or Teflon ring. Figure 3-14 illustrates the operational principle of a typical piston air compressor used to power a mechanical ventilator.

PTS:	1	REF:	Page 73

64.	Which of the following is (are) a small nebulizer compressor(s)?

1. Diaphragm

2. Liquid air

3. Rotary

4. Piston

| a. | 4 | c. | 1 and 2 |
| --- | --- | --- | --- |
| b. | 1 | d. | 1, 3, and 4 |

ANS:	B

A flexible diaphragm is attached to a piston to compress gas. As the piston moves down, the diaphragm is bent outward and gas is drawn through a one-way valve into the cylinder. Upward movement of the piston forces the gas out of the cylinder through a separate one-way outflow valve. Examples of diaphragm compressors are the Air Shields Diapump and the DeVilbiss small nebulizer compressor.

PTS:	1	REF:	Page 73

65.	Which of the following agencies makes recommendations for medical air supply?

| a. | ISO | c. | CGA |
| --- | --- | --- | --- |
| b. | NFPA | d. | Bureau of Medical Devices |

ANS:	B

See Box 3-8.

PTS:	1	REF:	Page 72, Box 3-8

66.	Which of the following statements about medical air supplies are false?

1. The air intake port must be located indoors.

2. The source of medical air must be from the outside atmosphere.

3. Most hospital bulk air supply systems use two compressors.

4. Backflow through the compressors that are cycled off must be prevented manually.

| a. | 1 and 4 | c. | 2 and 3 |
| --- | --- | --- | --- |
| b. | 1, 2, and 3 | d. | 3 and 4 |

ANS:	A

See Box 3-8.

PTS:	1	REF:	Page 72, Box 3-8

67.	Which of the following type(s) of air compressors is (are) used in bulk supply systems?

1. Piston

2. Rotary

3. Liquid air

4. Diaphragm

| a. | 1 and 4 | c. | 1 and 2 |
| --- | --- | --- | --- |
| b. | 1 and 3 | d. | 2 |

ANS:	C

To power a bulk air supply, either a piston or a rotary compressor is necessary. Liquid air is not used as a source for bulk supply. A diaphragm air compressor could not keep up with the requirements of a bulk system.

PTS:	1	REF:	Page 54, Box 3-2

68.	The NFPA requires that bulk oxygen systems be at least how many feet from parked vehicles?

| a. | 5 | c. | 15 |
| --- | --- | --- | --- |
| b. | 10 | d. | 20 |

ANS:	B

See Figure 3-11.

PTS:	1	REF:	Page 70, Figure 3-11

69.	If the working pressure of a bulk oxygen system is 45 psig, all pressure-relief valves should be set at _____ psig.

| a. | 45 | c. | 67 |
| --- | --- | --- | --- |
| b. | 50 | d. | 80 |

ANS:	C

All pressure-relief valves are set 50% higher than the system working pressure (e.g., set at 75 psi for a 50-psi system pressure).

PTS:	1	REF:	Page 74

70.	In the event of a fire in a hospital, which of the following might be necessary?

1. Provide supplemental oxygen to patients who require it.

2. Shut off oxygen zone valves to the affected area.

3. Shut off the main oxygen valve.

4. Check oxygen line pressure.

| a. | 3 | c. | 2 and 4 |
| --- | --- | --- | --- |
| b. | 1 and 2 | d. | 3 and 4 |

ANS:	B

In case of fire, affected zones can be isolated, thus preventing the problem from spreading to other areas of the hospital. And always remember patient safety in terms of applying the appropriate oxygen to each patient.

PTS:	1	REF:	Page 74

71.	Which of the following are safety features incorporated into a medical gas piping system?

1. Zone valves

2. Riser valves

3. Pressure-relief valves

4. In-line oxygen analyzers

| a. | 3 and 4 | c. | 1 and 4 |
| --- | --- | --- | --- |
| b. | 1 and 3 | d. | 1, 2, and 3 |

ANS:	D

See Figure 3-17.

PTS:	1	REF:	Page 75

72.	Which safety system(s) is (are) found at station outlets of a medical gas piping system?

1. Diameter Index Safety System (DISS)

2. American Standard Safety System (ASSS)

3. Pin Index Safety System

4. Quick Connect

| a. | 1 | c. | 2 and 3 |
| --- | --- | --- | --- |
| b. | 1 and 4 | d. | 2 and 4 |

ANS:	B

Station outlets are designed with safety systems that prevent the connection of incompatible devices. Two safety systems are currently available: the DISS and Quick-Connect adapters.

PTS:	1	REF:	Page 76

73.	The type of station outlet connection that uses noninterchangeable thread fittings to connect gas-powered devices to station outlets is known as:

| a. | regulator. | c. | Pin Index Safety System. |
| --- | --- | --- | --- |
| b. | quick-connect adapter. | d. | DISS. |

ANS:	D

Figure 3-20 shows an outlet that uses DISS. This system, which was designed by the CGA, uses noninterchangeable thread fittings to connect gas-powered devices to station outlets.

PTS:	1	REF:	Page 78

74.	Which of the following statements are true concerning station outlets?

1. Check valves are safety valves that close automatically when an adapter is disengaged from the outlet.

2. Station outlets do not have ASSS connections.

3. Quick-connect adapters use noninterchangeable thread fittings.

4. Check valves must hold a minimum of 200 psig.

| a. | 3 and 4 | c. | 2 and 4 |
| --- | --- | --- | --- |
| b. | 1, 3, and 4 | d. | 1 and 2 |

ANS:	D

Station outlets have safety valves that close automatically when an adapter is disengaged from the outlet (i.e., quick-connect adapters). The quick-connect adapters and the DISS are the two safety systems that can be at a station outlet.

PTS:	1	REF:	Page 76

75.	What percentage of oxygen does a typical molecular sieve concentrator provide when it is running at 2 L/min?

| a. | 100% | c. | 85% |
| --- | --- | --- | --- |
| b. | 90% | d. | 40% |

ANS:	B

The concentration of oxygen leaving the system depends on the flow rate set. For example, at flows less than 6 L/min, the gas contains approximately 92% to 97% oxygen.

PTS:	1	REF:	Page 79

76.	Which is true about the process of fractional distillation of liquid air?

| a. | Compressed air is a by-product. |
| --- | --- |
| b. | It produces pure liquid oxygen. |
| c. | Liquid nitrous oxide is produced. |
| d. | Concentrators use it to produce oxygen. |

ANS:	B

The fractional distillation of liquid air creates pure liquid oxygen. There are no by-products from this method. Oxygen concentrators take in room air and separate oxygen from nitrogen.

PTS:	1	REF:	Page 54, Box 3-1

77.	One liter of liquid oxygen is equivalent to _____ liters of gaseous oxygen.

| a. | 2.5 | c. | 348 |
| --- | --- | --- | --- |
| b. | 328 | d. | 860 |

ANS:	D

Oxygen expands to 860 times its liquid volume at 25° C and 1 atm; therefore, the total volume of gaseous oxygen available can be calculated by multiplying the number of liters of liquid oxygen by 860.

PTS:	1	REF:	Page 67

78.	Which of the following statements are true given that, on one side of a medical gas cylinder, the only markings to appear are 3 (tw) 84 + *.

1. The cylinder passed the hydrostatic test.

2. The cylinder must be retested after 5 years.

3. The cylinder must be retested after 10 years.

4. The cylinder was manufactured in March 1984.

5. Hydrostatic testing was performed in March 1984.

| a. | 2, 3, and 4 | c. | 1, 4, and 5 |
| --- | --- | --- | --- |
| b. | 2, 3, and 5 | d. | 1, 2, and 4 |

ANS:	D

See Figure 3-4.

PTS:	1	REF:	Page 61

79.	Which of the following statements reflect(s) the recommendations of the NFPA and CGA for storing cylinders outdoors?

1. Cylinders should not be stored in an area where the temperature exceeds 125° F.

2. Cylinders must be protected from the weather.

3. Full and empty cylinders should be kept separate.

4. Cylinders should not be stored outside.

| a. | 4 | c. | 2 and 3 |
| --- | --- | --- | --- |
| b. | 1 and 2 | d. | 1, 2, and 3 |

ANS:	D

See Box 3-3.

PTS:	1	REF:	Page 58, Box 3-3

80.	Which of the following large-cylinder safety recommendations is not appropriate?

| a. | Protective caps are not necessary during storage. |
| --- | --- |
| b. | Cylinders should be transported with protective caps. |
| c. | Cylinder carts used in the operating room must be grounded. |
| d. | Transportation must occur on an appropriate cart, onto which the cylinder is secured by a chain. |

ANS:	A

Large cylinders have a protective cap that fits over the valve stem. This cap should be kept on cylinders when moving or storing them.

PTS:	1	REF:	Page 58, Box 3-3

81.	Which of the following types of oxygen storage device are appropriate for home care?

1. Manifold

2. Compressor

3. Concentrator

4. Bulk oxygen system

5. Liquid oxygen cylinder

| a. | 2 and 5 | c. | 2, 3, and 5 |
| --- | --- | --- | --- |
| b. | 2 and 4 | d. | 1, 4, and 5 |

ANS:	A

Concentrators are used in the home care setting for patients who require low-flow oxygen. Liquid oxygen cylinders can allow the patient more time outside of the home during travel. Manifolds and bulk oxygen systems are not appropriate for home care. Compressors provide medical air, not oxygen.

PTS:	1	REF:	Page 79

82.	Which of the following have the fastest diffusion rate through the semipermeable membrane of an oxygen concentrator?

1. Carbon dioxide

2. Water vapor

3. Nitrogen

4. Oxygen

| a. | 1 and 2 | c. | 3 and 4 |
| --- | --- | --- | --- |
| b. | 1 and 3 | d. | 2 and 4 |

ANS:	D

Oxygen concentrators are devices that produce enriched oxygen from atmospheric air. Thus, oxygen and water vapor diffuse through these membranes faster than nitrogen.

PTS:	1	REF:	Page 77

83.	The concentration of oxygen leaving an oxygen concentrator depends on the:

| a. | number of sieves in the unit. |
| --- | --- |
| b. | number of compressors used. |
| c. | set flow rate of the gas exiting. |
| d. | size of the sodium-aluminum silicate pellets. |

ANS:	C

Atmospheric gases diffuse through the membrane at different rates. The rate at which a gas diffuses depends on its diffusion constant and solubility for the plastic membrane and the pressure gradient for the gas across the membrane.

PTS:	1	REF:	Page 77

84.	Bulk oxygen is produced through which of the following?

| a. | Molecular sieves | c. | Semipermeable membranes |
| --- | --- | --- | --- |
| b. | Fractional distillation | d. | Combustion of natural gas |

ANS:	B

Fractional distillation generates bulk oxygen. Molecular sieves and semipermeable membranes are used in oxygen concentrators. The combustion of natural gas produces carbon dioxide.

PTS:	1	REF:	Page 54

85.	Which of the following gases is used to treat singultus?

| a. | Air | c. | Nitrous oxide |
| --- | --- | --- | --- |
| b. | Oxygen | d. | Carbon dioxide |

ANS:	D

Carbon dioxide is used for the treatment of singultus (hiccups) and as a stimulant/depressant of the central nervous system.

PTS:	1	REF:	Page 55

86.	At –183° C, which of the following gases exists as a pale, bluish liquid that is slightly heavier than water?

| a. | Air | c. | Nitrous oxide |
| --- | --- | --- | --- |
| b. | Oxygen | d. | Carbon dioxide |

ANS:	B

Oxygen is an elemental gas that is colorless, odorless, and tasteless at normal temperatures and pressures. It makes up 20.9% of the Earth’s atmosphere by volume and 23.2% by weight. It constitutes approximately 50% of the Earth’s crust by weight. Oxygen is slightly heavier than air, having a density of 1.326kg/m3 at 21.1° C and 760 mm Hg (specific gravity = 1.105). At temperatures less than –183° C (–300° F), oxygen exists as a pale, bluish liquid that is slightly heavier than water.

PTS:	1	REF:	Page 54

87.	Which of the following gases may be used as a refrigerant?

| a. | Oxygen | c. | Carbon dioxide |
| --- | --- | --- | --- |
| b. | Nitric oxide | d. | Carbon monoxide |

ANS:	C

Solid carbon dioxide is used to refrigerate perishable materials during transport (e.g., food and laboratory specimens). Liquid carbon dioxide can be used as an expendable refrigerant and is used extensively as a fire-extinguishing agent in portable and stationary fire-extinguishing systems.

PTS:	1	REF:	Page 55

88.	Which of the letters points to the manufacturer’s mark?

| a. | A | c. | C |
| --- | --- | --- | --- |
| b. | B | d. | D |

ANS:	B

See Figure 3-4.

PTS:	1	REF:	Page 61

89.	Which size cylinder is currently used for the storage of nitric oxide?

| a. | 61.4 cubic feet | c. | 110 cubic feet |
| --- | --- | --- | --- |
| b. | 82 cubic feet | d. | 152 cubic feet |

ANS:	B

Before 1997, nitric oxide was supplied in cylinders with a volume capacity of 152 cubic feet. It is now supplied in smaller cylinders (82 cubic feet) with 626 CGA valve outlets.

PTS:	1	REF:	Page 56

90.	The cylinder color for nitric oxide is:

| a. | red. | c. | teal and black. |
| --- | --- | --- | --- |
| b. | light blue. | d. | brown and green. |

ANS:	C

See Table 3-4.

PTS:	1	REF:	Page 61

91.	Which gas law is applied in a fusible-plug pressure-relief valve?

| a. | Boyle’s | c. | Dalton’s |
| --- | --- | --- | --- |
| b. | Charles’ | d. | Gay-Lussac’s |

ANS:	D

The pressure-release valve allows some of the gas on top of the liquid to escape if the contents are warmed too much. This release of gas allows the gas within the container to expand, thus lowering the temperature. This maintains the gas under pressure between its boiling point and its critical temperature so that the majority of the reservoir’s contents will be maintained in the liquid state.

PTS:	1	REF:	Page 67

92.	The American Standard System connections for all life support gases are _____-handed and _____.

| a. | Left; internal | c. | Right; internal |
| --- | --- | --- | --- |
| b. | Left; external | d. | Right; external |

ANS:	D

Note that the connections for oxygen and other life-support gases are right-handed and external.

PTS:	1	REF:	Page 64

93.	Which of the following is the Pin Index Safety System pin position for oxygen?

| a. | A | c. | C |
| --- | --- | --- | --- |
| b. | B | d. | D |

ANS:	A

Recall that in this system, indexing is accomplished by the exact placement of two pins into holes in the post valve.

PTS:	1	REF:	Page 66, Figure 3-9

94.	An “E” size oxygen cylinder with 2200 psig has a set flow rate of 2 L/min. It will take _____ hours and _____ minutes until the gauge pressure reaches 400 psig.

| a. | 5; 30 | c. | 4; 30 |
| --- | --- | --- | --- |
| b. | 5; 6 | d. | 4; 12 |

ANS:	D

Amount of time left in cylinder = (cylinder pressure  cylinder factor)/flow rate of gas (liters/minute). 2200 – 400 = 1800 psig (the amount of gas that will be used). (1800  0.28)/2 = 252 minutes/60 = 4 hours 12 minutes.

PTS:	1	REF:	Page 67, Box 3-5

95.	Which of the following “E” size oxygen cylinders will last the longest?

Pressure                        Flow

(psig)                            (L/min)

| a. | 1600 3 | c. | 800 2 |
| --- | --- | --- | --- |
| b. | 1400 2.5 | d. | 400 1 |

ANS:	B

This answer was derived from the following formula:

1400  0.28 = 392/2.5 L/min = 156.8 minutes.

1400 psig at 2.5 L/min will last the longest compared with the other three.

PTS:	1	REF:	Page 67, Box 3-5

96.	An “H” size oxygen cylinder with 1600 psig has a set flow rate of 3 L/min. It will take _____ hours and _____ minutes to reach 300 psig.

| a. | 17; 24 | c. | 22; 40 |
| --- | --- | --- | --- |
| b. | 21; 25 | d. | 27; 54 |

ANS:	C

The same formula as described in the previous question is used here; however, you first have to subtract 300 psig from 1600 psig to get the exact duration for 1300 psig. (1300  3.14)/3 = 1360.7 minutes/60 = approximately 22 hours 40 minutes.

PTS:	1	REF:	Page 67, Box 3-5

97.	The following figure represents the components of which of the following?

| a. | Hydrostatic testing system | c. | Fractional distillation apparatus |
| --- | --- | --- | --- |
| b. | Bulk liquid oxygen system | d. | Alternating oxygen supply system |

ANS:	B

Recall also Figure 3-10.

PTS:	1	REF:	Page 68, Box 3-6

98.	Which of the following “G” size oxygen cylinders will run out of oxygen first?

Pressure              Flow

(psig)                (L/min)

| a. | 700 1.5 | c. | 1100 2.5 |
| --- | --- | --- | --- |
| b. | 900 1.0 | d. | 1600 3.0 |

ANS:	C

This answer was derived from the following formula:

The cylinder factor is 3.14. 1100 psig has the shortest duration at 1382 minutes, or 23 hours.

PTS:	1	REF:	Page 67, Box 3-5

99.	According to the NFPA, the minimum distance for a place of public assembly from a bulk oxygen storage system is how many feet?

| a. | 10 | c. | 25 |
| --- | --- | --- | --- |
| b. | 15 | d. | 50 |

ANS:	D

See Figure 3-11.

PTS:	1	REF:	Page 70

100.	Storage of a portable liquid oxygen system adjacent to a heat source will _____ the _____ of the oxygen.

| a. | Increase; pressure | c. | Decrease; pressure |
| --- | --- | --- | --- |
| b. | Increase; venting | d. | Decrease; venting |

ANS:	B

Liquid oxygen units should not be located adjacent to heat sources, which can accelerate the venting of oxygen.

PTS:	1	REF:	Page 72, Box 3-8

101.	A stationary liquid oxygen system contains 80 lb of oxygen when full. A home care patient is using it 8 hours each day, during sleep, at a rate of 3 L/min. At this usage, how many days will the liquid oxygen last?

| a. | 6 | c. | 19 |
| --- | --- | --- | --- |
| b. | 8 | d. | 27 |

ANS:	C

Use the liquid oxygen duration formula as given previously.

A liter of liquid oxygen weighs 2.5 lb, so: 80 lb/2.5 = 32 L.

Gaseous oxygen occupies a volume that is 860 times the volume of liquid oxygen, so: liters of liquid  860 = liters of gas.

Duration of supply (minutes) = gas supply remaining (in liters) ÷ flow (liters/minute).

Once you get the answer in minutes, you divide by 60 to obtain the number of hours. Then divide the number of hours by the usage, which is 8 hr/day; that gives you 19 days.

PTS:	1	REF:	Page 70, Box 3-7